## Fixture Schedule
Project: UCCS CYBERSECURITY & SPACE ISAC EXPANSION
Source: Sheet E7.1 ¦ Extracted: 2026-04-06 07:39
_row_key | TYPE | DESCRIPTION | MANUFACTURER | MODEL | LOAD | WATTS PER FOOT (FOR CONTINUOUS RUNS) | LAMP | DRIVER | VOLTAGE | MOUNTING | COMMENTS
L2A | L2A | 4"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 810/910 LUMEN PF, 4000K, DIM TO 1% | PEERLESS LIGHTING | OPM4 LLP 22FT MSL8 80CRI 40K I910LMF 810LMF DARK ZT 277 DCT F1/ | 299 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE
L2B | L2B | 4"x16' LINEAR PENDANT, DIRECT/INDIRECT, LED, 810/910 LUMEN PF, 4000K, DIM TO 1% | PEERLESS LIGHTING | OPM4 LLP 16FT MSL8 80CRI 40K I910LMF 810LMF DARK ZT 277 DCT F1/ | 218 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE
L3A | L3A | 4" SQUARE DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4SQ 40/15 AR LSS MVOLT GZ1 | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L3B | L3B | 6" SQUARE DOWNLIGHT, LED, 2500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4SQ 40/25 AR LSS MVOLT GZ1 | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L4A | L4A | 4" WIDE PERIMETER WALL-TO-WALL LINEAR RECESSED, ASSYMETRIC, LED, 875 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | P43-PSTD FLSH LED4 SO R(PER PLANS) TMW AWL D1R WTW SC X3B UNV DM01 |  | 10 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | REFER TO LIGHTING PLANS FOR REQUIRED LENGTH
L4B | L4B | 4" WIDE PERIMETER WALL-TO-POCKET LINEAR RECESSED, ASSYMETRIC, LED, 875 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | P43-PSTD FLSH LED4 SO R(PER PLANS) TMW AWL D1R WTW/LP SC X3B UNV DM01 |  | 10 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | REFER TO LIGHTING PLANS FOR REQUIRED LENGTH
L5A | L5A | 2'x4' ARCHITECTURAL RECESSED TROFFER, LED, 3000 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X4 80CRI 40K 3000LM MIN1 277 SWC ZT | 30 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L5B | L5B | 2'x4' ARCHITECTURAL RECESSED TROFFER, LED, 4000 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X4 80CRI 40K 4000LM MIN1 277 SWC ZT | 34 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L6A | L6A | 2'x2' ARCHITECTURAL FLAT PANEL RECESSED TROFFER, LED, 5000 LUMEN, 4000K, 90 CRI, DIM TO 1% | PEERLESS LIGHTING | VMMRA G 90CRI 40K 5000LM DARK ZT 277 C110 | 51 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7A | L7A | 4"x8' RECESSED HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R8 TMW BTW SC UNV X3 DM01 | 48 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7B | L7B | 4"x12' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 6' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R12 TMW BTW SC UNV X1 DM01 | 96 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 6' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING
L7C | L7C | 4"x20' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 10' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R20 TMW BTW SC UNV X1 DM01 | 160 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 10' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING
L7D | L7D | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 | 32 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7E | L7E | 4"x4' RECESSED HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R4 TMW BTW SC UNV X3 DM01 | 24 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7G | L7G | 4"x6' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R14 TMW BTW SC UNV X9 DM01 | 36 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7H | L7H | 4"x15' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R23 TMW BTW SC UNV X9 DM01 | 90 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7J | L7J | 4"x11' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R19 TMW BTW SC UNV X9 DM01 | 66 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7K | L7K | 4"x20' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R28 TMW BTW SC UNV X9 DM01 | 120 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7L | L7L | 4"x3' RECESSED SPECIALTY CEILING HARD-LID LINEAR, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 MO R3 TMW BTW SC UNV X9 DM01 | 18 VA | 6 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7N | L7N | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7NE | L7NE | 4"x4' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1% WITH INTEGRAL EGRESS BATTERY UNIT | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R4 TMW BTW SC UNV X1 DM01 EMHE | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L7P | L7P | 4"x14' RECESSED LINEAR, LED, 1000 LUMEN PF, 4000K, DIM TO 1%, SEPARATELY CONTROLLED 6' SECTIONS | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R12 TMW BTW SC UNV X1 DM01 | 112 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED | FIXTURE SHALL BE CONFIGURED SO THAT (2) 7' SECTIONS ARE INDEPENDENTLY CONTROLLED, IN A SINGLE SEAMLESS FIXTURE HOUSING
L7R | L7R | 4"x5' RECESSED HARD-LID LINEAR MUD-OVER FLANGE, LED, 720 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO4-REC FLSH LED4 SO R5 TMW BTW SC UNV X7 DM01 | 40 VA | 8 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L8A | L8A | 2'x2' ARCHITECTURAL RECESSED TROFFER, LED, 3300 LUMEN, 4000K, DIM TO 1% | MARK ARCHITECTURAL LIGHTING | WHSPR LCTR 2X2 80CRI 40K 3300LM MIN1 277 SWC ZT | 30 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L9A | L9A | 4' STRIP, LED, 4000 LUMEN, 4000K | LITHONIA LIGHTING | CSS L48 MVOLT 40K 80CRI ZACVH | 35 VA |  | LED | FIXED OUTPUT | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE
L10A | L10A | 4"x3' WALL MOUNTED LINEAR, LED, 675 LUMEN PF, 4000K | PRUDENTIAL LIGHTING | BIO-LIN LED4 MO R3 TMW AWL D1R NU SC UNV WS ND | 21 VA |  | LED | FIXED OUTPUT | 277 V | SURFACE, WALL | MOUNT @ 7'-0" AFF TO BOTTOM OF FIXTURE, CENTERED OVER MIRROR
L11A | L11A | 2'x4' FLAT PANEL RECESSED TROFFER, LED, 4800 LUMEN, 4000K, DIM TO 1% | LITHONIA LIGHTING | EPANL 2X4 4800LMHE 80CRI 40K MIN1 ZT MVOLT | 37 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L12A | L12A | 2"x24' RECESSED HARD LID LINEAR MUD-OVER FLANGE, LED, 390 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO2-REC LED4 LP R24 TMW SAL SC UNV X7 DM01 | 96 VA | 4 VA | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L13A | L13A | 3' SURFACE MOUNTED LINEAR WITH ADJUSTABLE OPTIC, LED, 5596 LUMEN, 4000K, DIM TO 1% | ELLIPTIPAR | S 315 R03M S 00 M 0K 0 840 TD | 41 VA | 14 VA | LED | 1% 0-10V DIMMING | 277 V | SURFACE
L14A | L14A | RGBW COLOR CHANGING TAPE LIGHT, LED, 425 LUMEN PF, WITH ALUMINUM MOUNTING CHANNEL | KELVIX | RGBW 1 24V / CH-502-A 2 CL CP EC |  | 8 VA | LED | 1% 0-10V DIMMING | 277 V | SURFACE
L15A | L15A | 2'x2' FLAT PANEL RECESSED TROFFER, LED, 3400 LUMEN, 4000K, DIM TO 1% | LITHONIA LIGHTING | EPANL 2X2 3400LMHE 80CRI 40K MIN1 ZT MVOLT | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L16A | L16A | 4" DIAMETER ROUND DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/1500 AR MWD LSS MVOLT GZ1 | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L16AE | L16AE | 4" DIAMETER ROUND DOWNLIGHT, LED, 1500 LUMEN, 4000K, DIM TO 1% WITH INTEGRAL EGRESS BATTERY UNIT | GOTHAM LIGHTING | EVO4 40/1500 AR MWD LSS MVOLT GZ1 EL | 14 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L16B | L16B | 4" DIAMETER ROUND DOWNLIGHT, LED, 2500 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/2500 AR WD LSS MVOLT GZ1 | 26 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L16C | L16C | 4" DIAMETER ROUND DOWNLIGHT, LED, 2000 LUMEN, 4000K, DIM TO 1% | GOTHAM LIGHTING | EVO4 40/2000 AR WD LSS MVOLT GZ1 | 20 VA |  | LED | 1% 0-10V DIMMING | 277 V | RECESSED
L18A | L18A | 4"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 843/281 LUMEN PF, 4000K, DIM TO 1% | FLUXWERX LIGHTING | APS R A C 40 B 22 G E1 M 03 | 187 VA | 9 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 10'-0" AFF TO BOTTOM OF FIXTURE
L19A | L19A | 26' MICRO WALL WASH, LED, 469 LUMEN PF, 4000K | PRUDENTIAL LIGHTING | MWR LED4 LO R26 TMW SC UNV WRM20" WRM1 TMW ND | 120 VA | 5 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | MOUNT @ 18" ABOVE TOP EDGE OF GRAPHIC TO BOTTOM OF FIXTURE
L20A | L20A | 5"x20' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R20 TMW BTW SCW ADC SC UNV CA48 DM01 | 240 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE
L20B | L20B | 5"x26' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R26 TMW BTW SCW ADC SC UNV CA48 DM01 | 312 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE
L20D | L20D | 5"x14' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R14 TMW BTW SCW ADC SC UNV CA48 DM01 | 168 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE
L20F | L20F | 5"x4' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R4 TMW BTW SCW ADC SC UNV CA48 DM01 | 48 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE
L20G | L20G | 5"x6' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R6 TMW BTW SCW ADC SC UNV CA48 DM01 | 72 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE
L20H | L20H | 5"x10' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R10 TMW BTW SCW ADC SC UNV CA48 DM01 | 120 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE
L20K | L20K | 5"x22' LINEAR PENDANT, DIRECT/INDIRECT, LED, 1025/575 LUMEN PF, 4000K, DIM TO 1% | PRUDENTIAL LIGHTING | BPRO5-LIN FLSH LED4 SO/LO R22 TMW BTW SCW ADC SC UNV CA48 DM01 | 264 VA | 12 VA | LED | 1% 0-10V DIMMING | 277 V | PENDANT | BOTTOM OF FIXTURE SHALL BE FLUSH WITH BOTTOM OF DOUBLE T STRUCTURE
XA | XA | EXIT SIGN, EDGE LIT, UNIVERSAL SURFACE MOUNT, GREEN LETTERING | SIGNTEX | CRS NB * G * BA * TW | 4 VA |  | LED | FIXED OUTPUT | 277 V | SURFACE | PROVIDE NUMBER OF FACES AND DIRECTIONAL ARROWS AS INDICATED ON PLANS; SINGLE-SIDED SIGNS SHALL HAVE CLEAR BACKGROUND, DOUBLE-SIDED FACES SHALL HAVE MIRRORED BACKGROUND

## _agentcm_meta (hidden)
schedule_id
schedule_type | fixture_schedule
sheet_id | 4fc12b63-dc42-438a-9056-3e2d48b9aeb8
exported_at | 2026-04-06T07:39:26.881041
schema_version | 1
agentcm_version | 1.0.0
project | UCCS CYBERSECURITY & SPACE ISAC EXPANSION
source_sheet | E7.1
row_count | 45
column_count | 11