## Fixture Schedule
Project: UCCS CYBERSECURITY & SPACE ISAC EXPANSION
Source: Sheet P7.1 ¦ Extracted: 2026-04-06 08:01
_row_key | SCHEDULE | FIXTURE TAG | DESCRIPTION | TYPE | CODE FLOW REQUIREMENTS | DESIGN FIXTURE FLOW | MANUFACTURER | MODEL | FLUSH-VALVE MANUFACTURER | FLUSH-VALVE MODEL | PLUMBING REMARKS
WC-1 | FLUSH VALVES | WC-1 | WATER CLOSET - WALL MOUNTED - ADA | MANUAL | 1.6 GPF | 1.1/1.6 GPF | AMERICAN STANDARD | 3351.101 | SLOAN | WES 111-1.6/1.1 | FIXTURE SHALL BE WATERSENSE LABELED. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
WC-2 | FLUSH VALVES | WC-2 | WATER CLOSET - WALL MOUNTED - ADA | MANUAL | 1.6 GPF | 1.28 GPF | AMERICAN STANDARD | 3351.101 | SLOAN | ROYAL 111-1.6 | VITREOUS CHINA. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
U-1 | FLUSH VALVES | U-1 | URINAL - WALL MOUNTED | MANUAL | 1 GPF | 0.125 GPF | ZURN | Z5755-U | SLOAN | ROYAL 186-0.125-DBP | VITREOUS CHINA, WALL-MOUNT. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
KS-1 | SINKS | KS-1 | KITCHEN SINK - UNDERMOUNT | MANUAL | 1.5 GPM | 3/4" | 2" | 2" | 2" | 1 | 2 | ELKAY | ELUHAD211550 | DELTA | D26C3934 | WITHOUT PERFECT DRAIN. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
L-1 | SINKS | L-1 | LAVATORY - UNDERMOUNT | HARD-WIRED | 0.5 GPM | 1/2" | 2" | 2" | 2" | 5 | 1 | AMERICAN STANDARD | 0496.300 | CHICAGO FAUCET | EQ-A12C-23ABCP | PROVIDE ASSE 1070 DEVICE. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
L-2 | SINKS | L-2 | LAVATORY - UNDERMOUNT | HARD-WIRED | 0.5 GPM | 1/2" | 2" | 2" | 2" | 14 | 1 | AMERICAN STANDARD | 0496.300 | CHICAGO FAUCET | EQ-A12C-23ABCP | REFER TO ARCH SHEET G.2.4.0 MEN AND WOMEN RESTROOM ALTERNATES. PROVIDE ASSE 1070 DEVICE. PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
MS-1 | SINKS | MS-1 | MOP SINK - FLOOR MOUNTED (RELOCATED) | MANUAL | N/A | 3/4" | 2" | 3" | 2" | 1 | 2 | REFER TO ARCH PLANS | N/A | N/A | N/A | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
DWH-1 | ELECTRIC WATER HEATER | DWH-1 | DOMESTIC WATER HEATER | JANITORS ROOM N108 | 72 °F | 14.4 | 6000 W | 208 V | 3 | AO SMITH | DEN-30 | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
EWH-1 | ELECTRIC WATER HEATER | EWH-1 | INSTANTANEOUS WATER HEATER | BREAKROOM N138 | 73 °F | 58 | 16050 W | 277 V | 1 | CHRONOMITE | R-58L/277 | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
GD-1 | GARBAGE DISPOSAL | GD-1 | GARBAGE DISPOSAL | 120 V | 1 | INSINKERATOR | BADGER 5 | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
DF-1 | MISCELLANEOUS | DF-1 | DRINKING FOUNTAIN WITH BOTTLE FILLER | N/A | 1/2" | 1 1/2" | 2" | 2" | ELKAY | EZSTLG8WSLK | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.
DF-2 | MISCELLANEOUS | DF-2 | DRINKING FOUNTAIN | N/A | 1/2" | 1 1/2" | 2" | 2" | ELKAY | EZSTLG8LC | PROVIDE MANUFACTURER AND MODEL NUMBER AS LISTED OR APPROVED EQUAL.

## _agentcm_meta (hidden)
schedule_id
schedule_type | fixture_schedule
sheet_id | 9b0fbff9-2665-4299-ab6b-720dd5867a3c
exported_at | 2026-04-06T08:01:37.015257
schema_version | 1
agentcm_version | 1.0.0
project | UCCS CYBERSECURITY & SPACE ISAC EXPANSION
source_sheet | P7.1
row_count | 12
column_count | 11